## PART A
A 1 | B | C | D | E | F | F
2 | -DUCT DESIGN SPECIFICATIONS | - | - | - | - | -
3 | Duct branch number or label | A->C | B->C | C->D | E->D | E->D
4 | Dry air volume flow, SCFM | 300 | 320 | 620 | 620 | 620
5 | Dry air mass flow, lbs/min | 22.476 | 23.9744 | 46.4504 | 46.4504 | 46.4504
6 | Air pres.@ branch start, "Hg | 29.921 | 29.921 | 29.3284 | 29.1718 | 29.921
7 | Dry bulb temp, 'F | 70 | 70 | 70 | 70 | 70
8 | Humidity ratio, lbH2O/lb air | 0.008 | 0.008 | 0.008 | 0.008 | 0.008
9 | Humid air vol. cuft/lb air | 13.5197 | 13.5197 | 13.7929 | 13.8669 | 13.5197
10 | Moist air density, lb/cuft | 0.074558 | 0.074558 | 0.073081 | 0.072691 | 0.074558
11 | Density correction factor | 0.99516 | 0.99516 | 0.97545 | 0.97025 | 0.99516
12 | Enthalpy, BTU/lb air | 25.5416 | 25.5416 | 25.5416 | 25.5416 | 25.5416
13 | Actual volume flow rate, ACFM | 303.8693 | 324.1272 | 640.6866 | 644.1251 | 627.9965
14 | slot area, sqft | #N/A | #N/A | #N/A | #N/A | #N/A
15 | slot velocity, fpm | #N/A | #N/A | #N/A | #N/A | #N/A
16 | VP slot, "H2O | #N/A | #N/A | #N/A | #N/A | #N/A
17 | Acceleration loss, 1 VP
18 | Slot entry loss, VP/slot
19 | Plenum loss factor, VP | 0 | 0 | 0 | 0 | 0
20 | Plenum SP, "H20 |  | #N/A
21 | Duct length, ft | 50 | 39 | 30 | 0 | 10
22 | Duct dia. inches | 3.5 | 3.5 | 5 | 5 | 5
23 | Duct area, sqft | 0.066813 | 0.066813 | 0.13635 | 0.13635 | 0.13635
24 | Duct Velocity, fpm | 4548.0338 | 4851.2361 | 4698.7098 | 4723.927 | 4605.6423
25 | Duct VP, "H2O | 1.282 | 1.4586 | 1.3412 | 1.3484 | 1.3146
26 | St. Duct friction, VP/100ft | 8.1968 | 8.1441 | 5.2928 | 5.2914 | 5.2981
27 | Elbow curvature, R/dia | 2 | 2
28 | Elbow loss factor, VP/elbow | 0.27 | 0.27
29 | Number of elbows in branch | 2 | 1.5
30 | -BRANCH LOSSES IN VP UNITS | - | - | - | - | -
31 | Acceleration loss, 1 VP/hood | 1 | 1
32 | Hood entry loss, VP/hood | 0.65 | 0.65
33 | Straight duct loss, VP | 4.0984 | 3.1762 | 1.5878 | 0 | 0.52981
34 | Elbow loss, VP | 0.54 | 0.405 | 0 | 0 | 0
35 | Branch entry loss factor, VP |  | 0.28
36 | Other losses in VP units
37 | Subtotal, lines 26 to 32 | 6.2884 | 5.5112 | 1.5878 | 0 | 0.52981
38 | -OTHER LOSSES IN "H2O UNITS | - | - | - | - | -
39 | Elevation change, ft | 0 | 0 | 0 | 0 | 10
40 | Air cleaner type |  |  | 36"Cyclone
41 | Rated volume flow, scfm |  |  | 1000
42 | Rated pressure drop, "H2O |  |  | 0
43 | Operating volume flow, acfm |  |  | 640.6866
44 | Operating pres. drop, "H2O |  |  | 0
45 | Loss from elev. change, "H2O | 0 | 0 | 0 | 0 | 0.1436
46 | Slot/Plenum loss, "H2O line 20 | 0 |  | 0 | 0 | 0
47 | Other losses in "H2O units
48 | Subtotal, lines 44 to 47 | 0 | 0 | 0 | 0 | 0.1436
49 | -SUMMARY OF LOSSES, "H2O | - | - | - | - | -
50 | VP losses, line 37 x VP ("H20) | 8.0615 | 8.0385 | 2.1296 | 0 | 0.69651
51 | Losses in "H2O units, line 48 | 0 | 0 | 0 | 0 | 0.1436
52 | Total branch loss, line 50+51 | 8.0615 | 8.0385 | 2.1296 | 0 | 0.84011
53 | DESIGN SUMMARY | - | - | - | - | -
54 | Cumulative loss @ branch end | 8.0615 | 8.0385 | 10.1796 | 10.1796 | 11.0197
55 | STATIC pres.@ branch end, "Hg | 29.3284 | 29.33 | 29.1718 | 29.1718 | 29.9828
56 | Fan total pressure, "H2O | - | - | - | - | 11.3577
57 | Fan static pressure, "H2O | - | - | - | - | 9.9679
57 | Fan brake horsepower @60% eff. | - | - | - | - | 1.8703
58 | STATIC pres.@ branch end, "H2o | 398.9389 | 398.9619 | 396.8093 | 396.8093 | 407.8405
<-- note the + sign in the formula, because it is downstream of the fan
<-- Design for part A of homework

## PART B
A 1 | B | C | D | E | F | F
2 | -DUCT DESIGN SPECIFICATIONS | - | - | - | - | -
3 | Duct branch number or label | A->C | B->C | C->D | E->D | E->D
4 | Dry air volume flow, SCFM | 300 | 320 | 620 | 620 | 620
5 | Dry air mass flow, lbs/min | 22.476 | 23.9744 | 46.4504 | 46.4504 | 46.4504
6 | Air pres.@ branch start, "Hg | 29.921 | 29.921 | 29.3284 | 28.8707 | 29.921
7 | Dry bulb temp, 'F | 70 | 70 | 70 | 70 | 70
8 | Humidity ratio, lbH2O/lb air | 0.008 | 0.008 | 0.008 | 0.008 | 0.008
9 | Humid air vol. cuft/lb air | 13.5197 | 13.5197 | 13.7929 | 14.0115 | 13.5197
10 | Moist air density, lb/cuft | 0.074558 | 0.074558 | 0.073081 | 0.071941 | 0.074558
11 | Density correction factor | 0.99516 | 0.99516 | 0.97545 | 0.96023 | 0.99516
12 | Enthalpy, BTU/lb air | 25.5416 | 25.5416 | 25.5416 | 25.5416 | 25.5416
13 | Actual volume flow rate, ACFM | 303.8693 | 324.1272 | 640.6866 | 650.8416 | 627.9965
14 | slot area, sqft | #N/A | #N/A | #N/A | #N/A | #N/A
15 | slot velocity, fpm | #N/A | #N/A | #N/A | #N/A | #N/A
16 | VP slot, "H2O | #N/A | #N/A | #N/A | #N/A | #N/A
17 | Acceleration loss, 1 VP
18 | Slot entry loss, VP/slot
19 | Plenum loss factor, VP | 0 | 0 | 0 | 0 | 0
20 | Plenum SP, "H20 |  | #N/A
21 | Duct length, ft | 50 | 39 | 20 | 10 | 10
22 | Duct dia. inches | 3.5 | 3.5 | 5 | 8 | 8
23 | Duct area, sqft | 0.066813 | 0.066813 | 0.13635 | 0.34907 | 0.34907
24 | Duct Velocity, fpm | 4548.0338 | 4851.2361 | 4698.7098 | 1864.5254 | 1799.079
25 | Duct VP, "H2O | 1.282 | 1.4586 | 1.3412 | 0.2079 | 0.2006
26 | St. Duct friction, VP/100ft | 8.1968 | 8.1441 | 5.2928 | 3.2745 | 3.2803
27 | Elbow curvature, R/dia | 2 | 2
28 | Elbow loss factor, VP/elbow | 0.27 | 0.27
29 | Number of elbows in branch | 2 | 1.5
30 | -BRANCH LOSSES IN VP UNITS | - | - | - | - | -
31 | Acceleration loss, 1 VP/hood | 1 | 1
32 | Hood entry loss, VP/hood | 0.65 | 0.65
33 | Straight duct loss, VP | 4.0984 | 3.1762 | 1.0586 | 0.32745 | 0.32803
34 | Elbow loss, VP | 0.54 | 0.405 | 0 | 0 | 0
35 | Branch entry loss factor, VP |  | 0.28
36 | Other losses in VP units
37 | Subtotal, lines 26 to 32 | 6.2884 | 5.5112 | 1.0586 | 0.32745 | 0.32803
38 | -OTHER LOSSES IN "H2O UNITS | - | - | - | - | -
39 | Elevation change, ft | 0 | 0 | 0 | 0 | 10
40 | Air cleaner type |  |  | MedCyclone
41 | Rated volume flow, scfm |  |  | 1000
42 | Rated pressure drop, "H2O |  |  | 12
43 | Operating volume flow, acfm |  |  | 640.6866
44 | Operating pres. drop, "H2O |  |  | 4.8048
45 | Loss from elev. change, "H2O | 0 | 0 | 0 | 0 | 0.1436
46 | Slot/Plenum loss, "H2O line 20 | 0 |  | 0 | 0 | 0
47 | Other losses in "H2O units
48 | Subtotal, lines 44 to 47 | 0 | 0 | 4.8048 | 0 | 0.1436
49 | -SUMMARY OF LOSSES, "H2O | - | - | - | - | -
50 | VP losses, line 37 x VP ("H20) | 8.0615 | 8.0385 | 1.4197 | 0.068075 | 0.065803
51 | Losses in "H2O units, line 48 | 0 | 0 | 4.8048 | 0 | 0.1436
52 | Total branch loss, line 50+51 | 8.0615 | 8.0385 | 6.2246 | 0.068075 | 0.20941
53 | DESIGN SUMMARY | - | - | - | - | -
54 | Cumulative loss @ branch end | 8.0615 | 8.0385 | 14.2746 | 14.3427 | 14.5521
55 | STATIC pres.@ branch end, "Hg | 29.3284 | 29.33 | 28.8707 | 28.8657 | 29.9364
56 | Fan total pressure, "H2O | - | - | - | - | 15.1547
57 | Fan static pressure, "H2O | - | - | - | - | 14.9382
57 | Fan brake horsepower @60% eff. | - | - | - | - | 2.4956
58 | STATIC pres.@ branch end, "H2o | 398.9389 | 398.9619 | 392.7143 | 392.6463 | 407.2098
<-- note the + sign in the formula, because it is downstream of the fan
<-- Design for part A of homework

## PART C
2 | -DUCT DESIGN SPECIFICATIONS | - | - | - | - | -
3 | Duct branch number or label | A->C | B->C | C->D | E->D | E->D
4 | Dry air volume flow, SCFM | 300 | 320 | 620 | 620 | 620
5 | Dry air mass flow, lbs/min | 22.476 | 23.9744 | 46.4504 | 46.4504 | 46.4504
6 | Air pres.@ branch start, "Hg | 24.1 | 24.1 | 23.7038 | 23.1876 | 29.921
7 | Dry bulb temp, 'F | 70 | 70 | 70 | 70 | 70
8 | Humidity ratio, lbH2O/lb air | 0.008 | 0.008 | 0.008 | 0.008 | 0.008
9 | Humid air vol. cuft/lb air | 16.7852 | 16.7852 | 17.0658 | 17.4457 | 13.5197
10 | Moist air density, lb/cuft | 0.060053 | 0.060053 | 0.059066 | 0.057779 | 0.074558
11 | Density correction factor | 0.80156 | 0.80156 | 0.78838 | 0.77121 | 0.99516
12 | Enthalpy, BTU/lb air | 25.5416 | 25.5416 | 25.5416 | 25.5416 | 25.5416
13 | Actual volume flow rate, ACFM | 377.2644 | 402.4154 | 792.7116 | 810.36 | 627.9965
14 | slot area, sqft | #N/A | #N/A | #N/A | #N/A | #N/A | elevation (ft) | 5280
15 | slot velocity, fpm | #N/A | #N/A | #N/A | #N/A | #N/A | Std Pressure | 29.921 | inches Hg
16 | VP slot, "H2O | #N/A | #N/A | #N/A | #N/A | #N/A | Press_at alt | 24.0989 | inches Hg
17 | Acceleration loss, 1 VP
18 | Slot entry loss, VP/slot
19 | Plenum loss factor, VP | 0 | 0 | 0 | 0 | 0
20 | Plenum SP, "H20 |  | #N/A
21 | Duct length, ft | 50 | 39 | 20 | 10 | 10
22 | Duct dia. inches | 4 | 4 | 5.5 | 10 | 10
23 | Duct area, sqft | 0.087266 | 0.087266 | 0.16499 | 0.54541 | 0.54541
24 | Duct Velocity, fpm | 4323.1356 | 4611.3446 | 4804.6616 | 1485.768 | 1151.4106
25 | Duct VP, "H2O | 0.93296 | 1.0615 | 1.1334 | 0.10602 | 0.082165
26 | St. Duct friction, VP/100ft | 7.0761 | 7.0306 | 4.7516 | 2.5795 | 2.6126
27 | Elbow curvature, R/dia | 2 | 2
28 | Elbow loss factor, VP/elbow | 0.27 | 0.27
29 | Number of elbows in branch | 2 | 1.5
30 | -BRANCH LOSSES IN VP UNITS | - | - | - | - | -
31 | Acceleration loss, 1 VP/hood | 1 | 1
32 | Hood entry loss, VP/hood | 0.65 | 0.65
33 | Straight duct loss, VP | 3.5381 | 2.7419 | 0.95032 | 0.25795 | 0.26126
34 | Elbow loss, VP | 0.54 | 0.405 | 0 | 0 | 0
35 | Branch entry loss factor, VP |  | 0.28
36 | Other losses in VP units
37 | Subtotal, lines 26 to 32 | 5.7281 | 5.0769 | 0.95032 | 0.25795 | 0.26126
38 | -OTHER LOSSES IN "H2O UNITS | - | - | - | - | -
39 | Elevation change, ft | 0 | 0 | 0 | 0 | 10
40 | Air cleaner type |  |  | 36"Cyclone
41 | Rated volume flow, scfm |  |  | 1000
42 | Rated pressure drop, "H2O |  |  | 12
43 | Operating volume flow, acfm |  |  | 792.7116
44 | Operating pres. drop, "H2O |  |  | 5.945
45 | Loss from elev. change, "H2O | 0 | 0 | 0 | 0 | 0.1436
46 | Slot/Plenum loss, "H2O line 20 | 0 |  | 0 | 0 | 0
47 | Other losses in "H2O units
48 | Subtotal, lines 44 to 47 | 0 | 0 | 5.945 | 0 | 0.1436
49 | -SUMMARY OF LOSSES, "H2O | - | - | - | - | -
50 | VP losses, line 37 x VP ("H20) | 5.3441 | 5.3892 | 1.0771 | 0.027349 | 0.021466
51 | Losses in "H2O units, line 48 | 0 | 0 | 5.945 | 0 | 0.1436
52 | Total branch loss, line 50+51 | 5.3441 | 5.3892 | 7.0221 | 0.027349 | 0.16507
53 | DESIGN SUMMARY | - | - | - | - | -
54 | Cumulative loss @ branch end | 5.3441 | 5.3892 | 12.3887 | 12.4161 | 12.5811
55 | STATIC pres.@ branch end, "Hg | 23.7071 | 23.7038 | 23.1876 | 23.1856 | 29.9331
56 | Fan total pressure, "H2O | - | - | - | - | 16.3134
57 | Fan static pressure, "H2O | - | - | - | - | 16.176
57 | Fan brake horsepower @60% eff. | - | - | - | - | 2.6864
58 | STATIC pres.@ branch end, "H2o | 322.4762 | 322.4311 | 315.409 | 315.3816 | 407.1655
<-- note the + sign in the formula, because it is downstream of the fan
<-- Design for part C of homework
Elevation pressure calc below