## Sheet2
A 1 | B | C | D | E | F
2 | -DUCT DESIGN SPECIFICATIONS | - | - | - | -
3 | Duct branch number or label | A->C | B->C | C->D | E->D
4 | Dry air volume flow, SCFM | 4880 | 1000 | 5880 | 5880

## Sheet1
A 1 | B | C | D | E | F | F
2 | -DUCT DESIGN SPECIFICATIONS | - | - | - | - | -
3 | Duct branch number or label | A->C | B->C | C->D | E->D | E->D
4 | Dry air volume flow, SCFM | 1020 | 2250 | 3270 | 3270 | 3270
5 | Dry air mass flow, lbs/min | 76.4184 | 168.57 | 244.9884 | 244.9884 | 244.9884
6 | Air pres.@ branch start, "Hg | 29.921 | 29.921 | 29.8317 | 29.6727 | 29.921
7 | Dry bulb temp, 'F | 70 | 400 | 297.0642 | 297.0642 | 297.0642
8 | Humidity ratio, lbH2O/lb air | 0.008 | 0.04 | 0.030018 | 0.030018 | 0.030018
9 | Humid air vol. cuft/lb air | 13.5197 | 23.0554 | 20.0491 | 20.1565 | 19.9893
10 | Moist air density, lb/cuft | 0.074558 | 0.045109 | 0.051375 | 0.051101 | 0.051528
11 | Density correction factor | 0.99516 | 0.60209 | 0.68573 | 0.68207 | 0.68778
12 | Enthalpy, BTU/lb air | 25.5416 | 145.648 | 107.1637 | 107.1637 | 107.1637
13 | Actual volume flow rate, ACFM | 1033.1556 | 3886.457 | 4911.8044 | 4938.1205 | 4897.1478
14 | slot area, sqft | 1 | #N/A | #N/A | #N/A | #N/A
15 | slot velocity, fpm | 1033.1556 | #N/A | #N/A | #N/A | #N/A
16 | VP slot, "H2O | 0.066154 | #N/A | #N/A | #N/A | #N/A
17 | Acceleration loss, 1 VP | 1
18 | Slot entry loss, VP/slot | 1.78
19 | Plenum loss factor, VP | 2.78 | 0 | 0 | 0 | 0
20 | Plenum SP, "H20 | 0.18391 | #N/A
21 | Duct length, ft | 15 | 55 | 25 | 75 | 30
22 | Duct dia. inches | 8 | 14 | 16 | 16 | 16
23 | Duct area, sqft | 0.34907 | 1.069 | 1.3963 | 1.3963 | 1.3963
24 | Duct Velocity, fpm | 2959.7751 | 3635.5555 | 3517.8238 | 3536.6713 | 3507.3267
25 | Duct VP, "H2O | 0.54293 | 0.4956 | 0.52848 | 0.53131 | 0.52691
26 | St. Duct friction, VP/100ft | 3.121 | 1.584 | 1.3416 | 1.3412 | 1.3418
27 | Elbow curvature, R/dia |  | 2
28 | Elbow loss factor, VP/elbow |  | 0.27
29 | Number of elbows in branch |  | 1
30 | -BRANCH LOSSES IN VP UNITS | - | - | - | - | -
31 | Acceleration loss, 1 VP/hood | 1 | 1
32 | Hood entry loss, VP/hood | 0.25 | 0.29
33 | Straight duct loss, VP | 0.46815 | 0.87123 | 0.3354 | 1.0059 | 0.40254
34 | Elbow loss, VP | 0 | 0.27 | 0 | 0 | 0
35 | Branch entry loss factor, VP | 0.18
36 | Other losses in VP units
37 | Subtotal, lines 26 to 32 | 1.8982 | 2.4312 | 0.3354 | 1.0059 | 0.40254
38 | -OTHER LOSSES IN "H2O UNITS | - | - | - | - | -
39 | Elevation change, ft | 0 | 0 | 0 | 0 | 30
40 | Air cleaner type |  |  | 36"Cyclone
41 | Rated volume flow, scfm |  |  | 5000
42 | Rated pressure drop, "H2O |  |  | 3
43 | Operating volume flow, acfm |  |  | 4911.8044
44 | Operating pres. drop, "H2O |  |  | 1.9852
45 | Loss from elev. change, "H2O | 0 | 0 | 0 | 0 | 0.29774
46 | Slot/Plenum loss, "H2O line 20 | 0.18391 |  | 0 | 0 | 0
47 | Other losses in "H2O units
48 | Subtotal, lines 44 to 47 | 0.18391 | 0 | 1.9852 | 0 | 0.29774
49 | -SUMMARY OF LOSSES, "H2O | - | - | - | - | -
50 | VP losses, line 37 x VP ("H20) | 1.0306 | 1.2049 | 0.17725 | 0.53447 | 0.2121
51 | Losses in "H2O units, line 48 | 0.18391 | 0 | 1.9852 | 0 | 0.29774
52 | Total branch loss, line 50+51 | 1.2145 | 1.2049 | 2.1625 | 0.53447 | 0.50984
53 | DESIGN SUMMARY | - | - | - | - | -
54 | Cumulative loss @ branch end | 1.2145 | 1.2049 | 3.3722 | 3.9067 | 4.4165
55 | STATIC pres.@ branch end, "Hg | 29.8317 | 29.8324 | 29.6727 | 29.6334 | 29.9585
56 | Fan total pressure, "H2O | - | - | - | - | 6.4751
57 | Fan static pressure, "H2O | - | - | - | - | 5.6962
57 | Fan brake horsepower @60% eff. | - | - | - | - | 8.3149
58 | STATIC pres.@ branch end, "H2o | 405.7859 | 405.7955 | 403.6234 | 403.089 | 407.5102
This is the spreadsheet given in Figure 4, the example problem from Koshland & Yost, Appl IH, V2(5):1987. The yellow cells are the ones that allow (or require) inputs or modification from the user to adapt it to a new problem. Note that some yellow cells contain formulas to account for mass balance in the system. Others are for duct information, and contain numeric values. The other cells that are not highlighted typically do not require modification.
MGY
<-- note the + sign in the formula, because it is downstream of the fan
<-- Note the formulas for mains to describe mass balance in the system